ELECTRICITY DEPARTMENT

(GOVERNMENT OF GOA)

DISTRIBUTION TRANSFORMER

SERVICE - BOOK

SOME DO-NOTS ABOUT THE DISTRIBUTION TRANSFORMERS

- Never allow transformer to be overloaded more then 5 to 10%

- Always avoid unbalance loading on phases.

- Never use fuses higher than the prescribed rates on HT and LT sides. The prescribed ratings of the fuses for HT and LT are given below.

|  | HT (11KV) | LT |  |
| --- | --- | --- | --- |
| Transformer Capacity | Size of HG Fuse in amps. | Size of TC Fuse wire in SWG | Size of TC Fuse wire in SWG upto 100. A |
| 25 kVA 50 kVA 63 K VA 100 k VA 160 k VA 200 k VA | 1 2.5 3 5 7.5 10 A | 38 33 33 32 30 26 | 21 18 or 2 of 20 2 of 20 140 amps HRC 225 amps HRC 280 amps HRC |

- Earthing connections should never be done in loose manner, simply

twisting of GI wires would be dangerous. The earthling connections

should as far as possible be done by using continuous wire or by providing

suitable connectors. It should be endured that these connections are tightened rigidly.

- Never keep the breather pipe open or exposed.

- Never charge the transformer with voltage more than primary voltage

rating.

- Do not ignore safety rules during maintenance work of distribution

transformers.

Location Code       Year of Issue       Manufg. Company        Origin (Area stores)

Item Code

TRANSFORMER

SERVICE-BOOK

- This transformer service book shall be issued with new transformer from store and shall move with transformer. It is therefore necessary that whenever the transformer is shifted from one region to another the book shall also be transferred with due acknowledgements.

Transformer service books for existing transformer will be supplied by concerned division.

- In case of failures/proposals for write off. Etc the book shall accompany the proposals.

- The book should not normally be sent with any report unless specifically

asked for. Only relevant extracts should accompany the reports.

- An incorrect/false entries in the book will lead to attraction of strict disciplinary action.

INDEX

| Sr. No | Particulars | Page No | Entries to be made by |
| --- | --- | --- | --- |
| 1 | Transformer History A. Transformer Name Plate B. Purchase / Issue C. Movements | 1 2 3 | AE/AEE (Stores) for new transformer & AE/AEE field Sub-div for existing Transformer. AE/AEE, SD-II, Stores Division AE/AEE, SD-II Stores Division |
| 2 | Transformer First Inspection Report | 4 | AE/AEE, SD-II, Stores Division |
| 3 | Insulation resistance values at the time of issue | 06 | AE/AEE, SD-II, Stores Division |
| 4 | (a) First Installation details (b)Subsequent details | 07 08 | AE/AEE (O&M) Division AE/AEE (O&M) Division |
| 5.1 | Loading on the transformers monthly | 09 | JE/AE/AEE (O&M) Division |
| 5.2 | TR centre Earth Resistance values quarterly | 10 | JE/AE/AEE (O&M) Division |
| 5.3 | Oil testing Details quarterly | 11 | JE/AE/AEE (O&M) Division |
| 5.4 | I.R values measured quarterly | 12 | JE/AE/AEE (O&M) Division |
| 5.5 | Inspection particulars monthly | 13 | JE/AE/AEE IV Division |
| 6 | Preventive Maintenance done | 14 | AEE / JE |
| 7 | Important Observations Incidents | 15 | JE/AE/AEE Sub-Div |
| 8 | Inspection report incase of failure of transformers | 16 | AE/ARR Sub-div Main |
| 9 | Annexure I, II & III for Testing etc. | 17 |  |

  - TRANSFORMER HISTORY SHEET

- TRANSFORMER NAME PLATE DETAILS

KVA ………………………….       TYPE OF COOLING……………ON

Name of Manufacturer________________               : % Impedance________________

Primary Volts___________________Volts              : Vector group_________________

Secondary _____________________Volts.              : Weight of Core_______________

Primary Current_________________Amps.             : & Winding _______________kg.

Secondary Current ______________  Amps.            : Weight of Oil _____________kg.

Primary Phase ___________________3                    : Oil in Litres _____________Ltrs

: Total Weight ______________kg

Secondary Phase _________________3                    : Maker’s Serial

Number                      ________

YEAR OF MANUFACTURE

TAPPING

| SI No of Tap Position | Percentage | PRIMARY | SECONDARY |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |
| 6 |  |  |  |

Signature:-

Name:-

Assistant Ex. Engineer / Assistant Engineer

- TRANSFORMER HISTORY SHEET

- PURCHASE / ISSUE DETAILS

i)  ORDER NO. AND DATE                       ……………………………………………..

ii)  DATE OF RECEIPT IN STORES          …………………………………………….

iii) ISSUE INDENT NO                               . …………Date……………………………

iv) GATE PASS NO                                      …………Date ……………………………

v)  GUARANTEE PERIOD                          ………………………………………….

vi) DATE OF EXPIRY OF

GUARANTEE PERIOD                        ……………………………………………

vii) I.R. VALUES IN MEGAOHMS (ON RECEIPT AT STORES/AT THE TIME OF

ISSUE)

ON Receipt                                      At the time of issue

a) HV terminals to                 …………………….                        ……………………………

Tank Body earth

Terminal.

b) LV. Terminal to Tank        ……………………                         ……………………………

body earth terminal

c)   HV. Terminal to LV         ……………………                          …………………………..

terminal

d)   Ambient Temp. at             ……………………                         ……………………………

the time of taking

these values

e)   Voltage rating of the

megger used ………………………………….Volts.

Date:-

Signature:-

Name:-

Assistant Ex. Engineer / Assistant Engineer of Stores:

- TRANSFORMER HISTORY SHEET

© DETAILS OF MOVEMENT

| S. No. | I | II | III | IV | V |
| --- | --- | --- | --- | --- | --- |
| 1. S. No |  |  |  |  |  |
| 2. Shifted from |  |  |  |  |  |
| 3. Date of shifting |  |  |  |  |  |
| 4. Reason for Removal |  |  |  |  |  |
| 5. Received at |  |  |  |  |  |
| 6. Date of receipt |  |  |  |  |  |
| CONDITION OF TRANSFORMER |  |  |  |  |  |
| 7. Physical |  |  |  |  |  |
| 8.Oil |  |  |  |  |  |
| 9.Electrical |  |  |  |  |  |
| 10. Dated/Signature of Receiving Officer |  |  |  |  |  |

Signature:-

Name:-

Assistant Ex. Engineer / Assistant Engineer

4(b) DETAILS OF CHECKS AT CHANGED

PLACES OF INSTALLATION

1. Name of sub-station                           …………………………………………

Commissioning date                           …………………………………………

2.  Place of installation village               . ………………………………………..

3.  Name of Distribution centre            .  . .…………………………………………

4.  Earth Resistance of sub-station      ……………………………………………..

- ………………………………………………

- ………………………………………………

- ……………………………………………….

5.   Protection provided on

H.T    DO/HG fuse                       ……………………………………amps

L.T           ICTP Switch fuse         ……………………………………amps

…………………………………….

…………………………………….

6.   Lighting Protection (Lightning arrestors)

On H.T           Yes / No.                   Rating ……………..kV…………….kA

On L.T            Yes / No.                  Rating………………kV…………….Ka

Signature of Assistant Engineer /Junior Engineer

………………………………………………….

Place……………………………………………

Date…………………………………………….

- TRANSFORMER FIRST INSPECTION REPORT

(These checkings should be personally done & recorded by the AE S.D II (Store)

1 (i)   MAKE            :       __________________________

(ii)  RATING          :       __________________________KVA

(iii)  SERIAL No.   :       __________________________

2.   CHECK LIST FOR PHYSICAL DAMAGE TO

| (External Parts) | Nature of Defect | Defect Corrected on |
| --- | --- | --- |
| (i) Main Tank |  |  |
| (ii) Cooling Tubes Detachable Radiators |  |  |
| (iii) Conservator Tank |  |  |
| (iv) Breather Attachment |  |  |
| (v) Bushings |  |  |
| (vi) Drain Valves / Filter Valves |  |  |
| (vii) Explosion Vent |  |  |
| (viii) Oil Level Indicator |  |  |
| (ix) Tap Operating Handle/Wheel |  |  |
| (x) Ratio Change Over Handle |  |  |

- CHECK LIST FOR OIL LEAKAGE FOEM WELDED JOINTS:-

|  | Leakage Marked | Repaired On |
| --- | --- | --- |
| (i) Main Tank |  |  |
| (ii) Cooling tubes Radiators |  |  |
| (iii) Flanges of (a) Drain Valve (b) Tap Changer Shaft © Explosion Vent |  |  |
| (iv) Thermometer Pocket: |  |  |
| (v) Air Release Plug & |  |  |
| (vi) Conservator Tank |  |  |

CHECK LIST FOR DETERIORATION OF GASKETS OF

|  | Noted | Replaced on |
| --- | --- | --- |
| Main Tank Cover |  |  |
| HV / LV Bushings |  |  |
| Drain Valve / Filter Valves |  |  |
| Tap Changer Shaft |  |  |
| Explosion Vent |  |  |
| Joint between Main Tank & Conservator |  |  |
| Flange of Breather Attachment & |  |  |
| Breather Housing Cover |  |  |

Check

|  | Noted | Action taken by S.D.O. |
| --- | --- | --- |
| Corrision of Tank |  |  |
| Corrosion of Conservator |  |  |

Name:

Signature of Assistant Engineer / Assistant Ex. Engineer Store

3. INSULATION RESISTANCE VALUES AT THE TIME OF ISSUE TO THE

FIELD UNIT FOR INSTALLATION

DATE: _____________________________

(1) IR VALUE

HV to LV +E  _____________________M. ohr

LV to HV +E ______________________M ohr

HV – LV    ________________________M. ohr

AT _______________oC WITH __________________ 1000 VOLTS MEGGER

A.E / A.E.E. (Sub. Div)                                                           A.E.E / A.E.      Store

- (a) FIRST INSTALLATION DETAILS

1. Name of sub-station                           …………………………………………

Commissioning date                           …………………………………………

2.  Place of installation village               . ………………………………………..

3.  Name of Distribution centre            .  . .…………………………………………

4.  Earth Resistance of sub-station      ……………………………………………..

/T/C                                                      …………………………………………….

1………………………………………………

2………………………………………………

3……………………………………………….

5.   Protection provided on

H.T.           HG fuse                                …………………………… amps

L.T            ICTP Switch fuse (main)      …………………………… amps

First feeder fuse                    …………………………….amps

Second feeder fuse                …………………………….amps

Third feeder fuse                  …………………………….amps

Fourth feeder fuse               ……………………………. amps

6      Lightning Protection (Lightning arrestors)

On H.T                  Yes/No                 Rating  _________ Kv ________Ka

Signature of AE/AEE/Junior Engineer

______________________________

Place

Date

6.   PREVENTIVE MAINTENANCE AND REMEDIAL ACTIONS TAKEN BY THE JUNIOR ENGINEER AND S.D.O.

Details of work carried out viz.

| Sr. No. | Date | Topping of oil | Filteration of oil | Drying of transformers | Arresting oil leakage etc. | Changing of silica gel |
| --- | --- | --- | --- | --- | --- | --- |

Date:___________________

Signature of AE/AEE/Junior Engineer

______________________________

Place

Date

- IMPORTANT OBSERVATIONS / INCIDENTS

| Date | Event | Analysis / Remark |
| --- | --- | --- |

Signature of AE/AEE/Junior Engineer

______________________________

Place

Date

- INSPECTION REPORT

(In case of transformer failure)  (as found condition)

- Date of failure                                                  ……………………….

- Time of failure                                                 ……………………….

- Location at which failed                                   ………………………

- Operation being done at the time of failure      ………………………

- IR measurement after failure                             ……………………...

(H.V. + L.V.)  to E                                    - Temp ºc ………………

HV to LV

Continuity between phases:

H T                                                            ………………………….

L T                                                            ………………………….

- Rating of fuses & their conditions              …………………………..

- Explosion heat (if any)                                ………………………….

- a. Dielectric strength of oil                              ………………………….

b. Smell (if noticed)                                         …………………………

After opening the transformer tank

- Condition of windings

Phase A                                                a ………………………

Phase B                                                b………………………

Phase C                                                c………………………

- Metallic pieces filling (if any) found within the tank

- Displacement of windings (if any) noticed

- Damage to leads (if any)

- Damage to tap change circuit (if any)

- Observations on items as at page 7 A1-A5

8.   INSPECTION REPORT FAILED TRANSFORMERS